## Load Schedule
WAREHOUSE ELECTRICAL LOAD SCHEDULE & CONSUMPTION CALCULATOR
Site: Holy Builders Warehouse, Bintulu ¦ Incoming: 3-phase 60 A, 415 V ¦ Capacity 43.1 kVA / 36.7 kW
Key in the yellow cells only: Type (dropdown), Watts each, Qty, Hours/day, Days/month, Load %, Phase, Peak (Y/N). All other columns calculate.
PHASE BALANCE (A) | Phase R |  | Phase Y |  | Phase B |  | Phase check |  |  | Connected load (kW) | Est. max demand (kW) | Current/phase (A) | % of breaker | Monthly kWh | Monthly bill (RM)
Peak current per phase | 24.9435 |  | 23.9615 |  | 28.9502 |  | Balanced |  |  | SUPPLY CHECK: | OK - 20.8 kW headroom on the 60 A supply.
Imbalance | 17.23% | ← keep below 20% | [7 empty] | 29.39 | 15.856 | 25.9517 | 43.25% | 4793.84 | 1514.0288
No | Equipment / circuit description | Type | Watts each (W) | Qty | Hours / day | Days / month | Load % | Peak (Y/N) | Phase (R/Y/B/3P) | kWh/day | Connected kW | Demand kW | Current (A) | Monthly kWh | Monthly cost (RM) | Remarks
1 | LED spotlights - signage & front | Spotlight | 50 | 10 | 12 | 30 | 100% | Y | R | 6 | 0.5 | 0.5 | 2.4551 | 180 | 56.849 | Dusk to midnight
2 | LED high-bay lights - warehouse | Lighting | 150 | 40 | 10 | 26 | 100% | Y | 3P | 60 | 6 | 6 | 9.8203 | 1560 | 492.6916 | Spread over R/Y/B circuits
3 | LED tube lights - office & store | Lighting | 18 | 30 | 9 | 26 | 100% | Y | R | 4.86 | 0.54 | 0.54 | 2.6515 | 126.36 | 39.908
4 | Air-cond 2.5 hp - office 1 | Air-cond | 2300 | 1 | 9 | 26 | 70% | Y | R | 14.49 | 2.3 | 1.61 | 7.9053 | 376.74 | 118.985 | Compressor cycling ~70%
5 | Air-cond 2.0 hp - office 2 | Air-cond | 1800 | 1 | 9 | 26 | 70% | Y | B | 11.34 | 1.8 | 1.26 | 6.1868 | 294.84 | 93.1187
6 | Air-cond 1.5 hp - guard house | Air-cond | 1300 | 1 | 12 | 30 | 70% | Y | B | 10.92 | 1.3 | 0.91 | 4.4682 | 327.6 | 103.4652
7 | 13 A sockets - office general (per outlet) | 13A Socket | 200 | 12 | 9 | 26 | 50% | Y | B | 10.8 | 2.4 | 1.2 | 5.8922 | 280.8 | 88.6845 | Computers, printers, chargers
8 | 13 A socket - pantry kettle & fridge | 13A Socket | 2000 | 1 | 2 | 26 | 100% | N | R | 4 | 2 | 0 | 9.8203 | 104 | 32.8461
9 | 13 A sockets - warehouse power tools | 13A Socket | 1000 | 4 | 3 | 26 | 60% | Y | Y | 7.2 | 4 | 2.4 | 11.7843 | 187.2 | 59.123
10 | Forklift battery charger | Motor / Machinery | 6000 | 1 | 8 | 26 | 85% | Y | 3P | 40.8 | 6 | 5.1 | 8.3472 | 1060.8 | 335.0303
11 | Roller shutter motors | Motor / Machinery | 750 | 2 | 1 | 26 | 100% | N | 3P | 1.5 | 1.5 | 0 | 2.4551 | 39 | 12.3173
12 | CCTV, alarm, router | Other | 300 | 1 | 24 | 30 | 100% | Y | B | 7.2 | 0.3 | 0.3 | 1.473 | 216 | 68.2188 | 24-hour load
13 | Water pump 1 hp | Motor / Machinery | 750 | 1 | 2 | 30 | 90% | N | R | 1.35 | 0.75 | 0 | 3.3143 | 40.5 | 12.791
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
| TOTAL | [8 empty] | 180.46 | 29.39 | 19.82 |  | 4793.84 | 1514.0288
SUMMARY BY TYPE
| Type | Items |  | Connected kW |  | Demand kW |  | Monthly kWh |  | % of kWh | Monthly cost (RM)
| Spotlight | 1 |  | 0.5 |  | 0.5 |  | 180 |  | 3.755% | 56.849
| Lighting | 2 |  | 6.54 |  | 6.54 |  | 1686.36 |  | 35.18% | 532.5997
| Air-cond | 3 |  | 5.4 |  | 3.78 |  | 999.18 |  | 20.84% | 315.569
| 13A Socket | 3 |  | 8.4 |  | 3.6 |  | 572 |  | 11.93% | 180.6536
| Fan | 0 |  | 0 |  | 0 |  | 0 |  | 0% | 0
| Motor / Machinery | 3 |  | 8.25 |  | 5.1 |  | 1140.3 |  | 23.79% | 360.1386
| Other | 1 |  | 0.3 |  | 0.3 |  | 216 |  | 4.506% | 68.2188
| TOTAL | 13 |  | 29.39 |  | 19.82 |  | 4793.84 |  | 100% | 1514.0288
| Annual energy (kWh) |  |  | 57526.08
| Annual electricity cost (RM) |  |  | 18168.3456
| Average cost (sen/kWh) |  |  | 31.5828
| Carbon footprint (t CO₂ / year) |  |  | 19.5589
Notes:
1. Watts each = nameplate / running watts of one unit (see Typical Ratings on the Settings sheet). Air-cond: use running kW, not cooling capacity.
2. Load % = fraction of rated watts actually drawn on average (air-cond compressor cycling ~70%, sockets 20-60%). Peak = Y if the item runs during the busiest hour.
3. Phase: R / Y / B for single-phase circuits, 3P for three-phase equipment. Keep the three phase currents within 20% of each other.
4. Current (A) per row is at full load %; the Supply Check applies the diversity factor from the Settings sheet.
5. Bill uses Sarawak Energy C1 block rates by default (change to C2 on the Settings sheet if a maximum-demand meter is installed). Verify rates against your latest bill.

## Settings & Tariff
WAREHOUSE ELECTRICAL LOAD CALCULATOR - SETTINGS
Yellow cells are inputs. Everything else calculates automatically.
1. INCOMING SUPPLY
Site name | Holy Builders Warehouse, Bintulu
Number of phases (1 or 3) | 3 |  | 3-phase incoming
Main incoming breaker rating | 60 | A | As given: 60 A
Line voltage | 415 | V | 415 V line-line for 3-phase; 240 V for single phase
Power factor | 0.85 |  | Typical mixed load 0.85; aircond/motors ~0.8
Diversity factor on peak loads | 0.8 |  | Not everything ticked "Peak" runs at full load together
Safe continuous loading of breaker | 80% | % | Good practice: keep continuous load ≤ 80% of breaker rating
Supply capacity (kVA) | 43.1281
Usable power at power factor (kW) | 36.6589
Safe continuous current per phase (A) | 48
2. TARIFF (Sarawak Energy)
Tariff: type C1 or C2 | C1 |  | C1 = commercial block rates (no demand meter, usual for 60 A). C2 = 24.5 sen/kWh + RM 16/kW max demand
C2 energy rate | 24.5 | sen/kWh
C2 maximum demand charge | 16 | RM/kW
C1 minimum monthly charge | 10 | RM
Taxes / levies on bill | 0% | % | Usually 0 for commercial in Sarawak
Default operating days per month | 26 | days
Grid carbon factor | 0.34 | kg CO₂/kWh | Sarawak grid (mostly hydro) - approx.
3. C1 BLOCK RATES (editable - verify against your latest bill)
Block | From kWh (excl.) | To kWh (incl.) | sen/kWh | kWh in block | Charge (RM)
1 | 0 | 100 | 20 | 100 | 20
2 | 100 | 200 | 24 | 100 | 24
3 | 200 | 10000 | 32 | 4593.84 | 1470.0288
4 | 10000 | 20000 | 31 | 0 | 0
5 | 20000 | 99999999 | 30 | 0 | 0
|  |  |  | C1 energy charge | 1514.0288
4. TYPICAL RATINGS (reference for the Watts column)
Equipment | Typical W each | Note
LED spotlight / floodlight | 50 | 30-100 W LED; halogen flood 500 W
LED high-bay light | 150 | 100-200 W
LED tube 4 ft | 18 | T8 LED
Fluorescent 2 x 36 W fitting | 90 | incl. ballast
Air-cond 1.0 hp | 900 | ~0.9 kW running
Air-cond 1.5 hp | 1300
Air-cond 2.0 hp | 1800
Air-cond 2.5 hp | 2300
Air-cond cassette 3.0 hp | 2800
13 A socket - general use allowance | 200 | per outlet, light use
13 A socket - kettle / water heater | 2000
13 A socket - computer & monitor | 150
13 A socket - fridge | 150 | running
Ceiling / wall fan | 75
HVLS fan 7.3 m | 1500
Forklift charger | 6000
Roller shutter motor | 750
Water pump 1 hp | 750