## Summary
WTP 20 m3/h x 6 h/day - Power Supply and Pump Sizing Summary
Shelter 18.3 m x 7.2 m x 3.6 m. 415 V 3-phase 50 Hz. All figures link to the calculation sheets.
Item | Value | Unit | Note
PUMP MOTORS
Raw Water Pump (duty + standby) - calculated motor | 2.2 | kW | 10 m3/h at 30 m
Raw Water Pump - drawing motor | 5.5 | kW
Backwash Pump (duty + standby) - calculated motor | 5.5 | kW | 30 m3/h at 30 m
Backwash Pump - drawing motor | 5.5 | kW
Treated Water Pump - calculated motor | 2.2 | kW | 12 m3/h at 30 m
Treated Water Pump - drawing motor | 5.5 | kW
Total installed pump motor kW (design basis) | 27.5 | kW | 5 motors
Motor FLC each (design basis, 415 V) | 10.0468 | A
Motor feeder MCCB (each) | 25 | A | 3P, with Star-Delta starter
Motor feeder cable (each) | 2.5 | mm2 | Cu XLPE/SWA/PVC 4-core
INCOMING SUPPLY
Total connected load | 33.96 | kW
Maximum demand | 27.9051 | kVA | Standby pumps excluded
Maximum demand current | 38.8217 | A
Design current incl. spare | 48.5272 | A
Recommended main MCCB | 63 | A | 4-pole
Main MCCB on drawing | 225 | A | 4P 225 A
Incoming cable | 16 | mm2 | Cu XLPE/SWA/PVC 4-core
Declared maximum demand for TNB | 35 | kVA
Standby generator (if required) | 40 | kVA
Estimated energy | 4302.4821 | kWh/month | Upper bound

## Inputs
Water Treatment Plant 20 m3/h - Electrical Design Inputs
Blue text = input (edit here). Black = formula. Yellow fill = assumption to be confirmed by the user/vendor.
Parameter | Value | Unit | Basis / Source | Std IEC motor kW | Std MCCB/MCB (A) | Cable size (mm2) | Ampacity (A) Cu XLPE/SWA/PVC 4-core, on tray, 30 C | Volt drop (mV/A/m)
SYSTEM PARAMETERS |  |  |  | 0.37 | 6 | 1.5 | 22 | 29
Supply voltage, line-to-line | 415 | V | TNB LV 3-phase 4-wire supply, per drawing 'Main Incoming 415V, 3PH, 50Hz' | 0.55 | 10 | 2.5 | 30 | 18
Frequency | 50 | Hz | Per drawing | 0.75 | 16 | 4 | 40 | 11
Single-phase voltage, line-to-neutral | 240 | V | Derived from line voltage | 1.1 | 20 | 6 | 52 | 7.3
Motor power factor at full load | 0.85 | - | Typical IE3 4-pole 5.5 kW motor at full load. Confirm from motor nameplate. | 1.5 | 25 | 10 | 71 | 4.4
Lighting / small-power power factor | 0.9 | - | Assumed. LED lighting and general sockets. | 2.2 | 32 | 16 | 94 | 2.8
Motor efficiency (IE3, 4-pole, 5.5 kW class) | 0.896 | - | IEC 60034-30-1 IE3 minimum, 4-pole, 5.5 kW = 89.6% | 3 | 40 | 25 | 124 | 1.75
Pump hydraulic efficiency at duty point | 0.65 | - | Assumed for end-suction centrifugal pumps of this size. Replace with value from vendor pump curve. | 4 | 50 | 35 | 153 | 1.25
Motor sizing margin on shaft power | 1.2 | - | Shaft power x 1.20 before selecting next standard IEC motor (common practice for pumps < 7.5 kW) | 5.5 | 63 | 50 | 185 | 0.93
Water density | 1000 | kg/m3 | Fresh water at 25 C | 7.5 | 80 | 70 | 236 | 0.63
Gravitational acceleration | 9.81 | m/s2 |  | 11 | 100 | 95 | 288 | 0.46
PROTECTION AND CABLE SIZING |  |  |  | 15 | 125 | 120 | 335 | 0.38
Breaker sizing factor - motor feeders (x FLC) | 2 | - | MCCB magnetic/thermal rating for motor circuits; overload protection is by the starter overload relay. Gives 25 A for a 5.5 kW motor, matching drawing. | 18.5 | 160 | 150 | 385 | 0.31
Breaker sizing factor - non-motor feeders (x FLC) | 1.25 | - | Standard 125% of design current | 22 | 200 | 185 | 440 | 0.25
Cable derating factor (grouping x ambient) | 0.87 | - | Assumed 35 C ambient, up to 3 circuits grouped on tray. Confirm against installation method. | 30 | 225 | 240 | 515 | 0.19
Max voltage drop - motor and sub-main feeders | 4% | % | 4% of nominal (MS IEC 60364 / BS 7671 guidance for power) |  | 250
Max voltage drop - lighting / small power | 3% | % | 3% of nominal |  | 320 | Cable ratings are indicative values for copper XLPE-insulated SWA/PVC 4-core cables on perforated tray (BS 7671 Table 4E4A order of magnitude). Verify against the cable manufacturer's catalogue before purchase.
Diversity factor - lighting and small power | 0.8 | - | Assumed |  | 400
Spare capacity on incoming supply | 0.25 | - | 25% allowance for future loads when selecting main MCCB and incoming cable
DOL starting current multiple (x FLC) | 6 | - | Typical squirrel-cage motor
Star-Delta starting current multiple (x FLC) | 2 | - | Approx. one-third of DOL starting current
Star-Delta threshold (motors at or above this use Star-Delta) | 4 | kW | Per drawing: Star-Delta recommended for 5.5 kW pumps
Electrical design basis for motor kW (Drawing / Calculated) | Drawing | - | 'Drawing' sizes feeders on the 5.5 kW motors shown. 'Calculated' uses the hydraulic calculation result on the Pump Sizing sheet.
OPERATING PROFILE
Plant running hours per day | 6 | h/day | Per drawing: 20 m3/h x 6 h/day = 120 m3/day
Operating days per month | 30 | days | Assumed
Electricity tariff (for estimate only) | 0.509 | RM/kWh | Assumed TNB Tariff C1 energy charge; replace with actual tariff

## Pump Sizing
Pump Hydraulic Power and Motor kW Required
P_hyd (kW) = rho x g x Q x H / (3,600 x 1,000). Shaft kW = P_hyd / pump eff. Motor = next standard IEC rating above shaft kW x margin.
No. | Tag | Service | Duty / Standby | Flow Q (m3/h) | Head H (m) | Hydraulic power (kW) | Pump eff. | Shaft power (kW) | Shaft x margin (kW) | Calculated motor (kW) | Drawing motor (kW) | Design motor (kW) | Motor eff. | PF | FLC (A) | Starter | Starting current (A) | Remarks
1 | P-01 | Raw Water Pump-1 (Duty) | Duty | 10 | 30 | 0.8175 | 0.65 | 1.2577 | 1.5092 | 2.2 | 5.5 | 5.5 | 0.896 | 0.85 | 10.0468 | Star-Delta | 20.0936 | Drawing: 10 m3/h, 25-30 m. Upper head used.
2 | P-02 | Raw Water Pump-2 (Standby) | Standby | 10 | 30 | 0.8175 | 0.65 | 1.2577 | 1.5092 | 2.2 | 5.5 | 5.5 | 0.896 | 0.85 | 10.0468 | Star-Delta | 20.0936 | Identical to P-01, 100% standby.
3 | P-08 | Backwash Pump (Duty) | Duty | 30 | 30 | 2.4525 | 0.65 | 3.7731 | 4.5277 | 5.5 | 5.5 | 5.5 | 0.896 | 0.85 | 10.0468 | Star-Delta | 20.0936 | Drawing: 25-30 m3/h, 25-30 m. Backwash flow 25-30 m3/h at 2.0 m/s.
4 | P-11 | Backwash Pump (Standby) | Standby | 30 | 30 | 2.4525 | 0.65 | 3.7731 | 4.5277 | 5.5 | 5.5 | 5.5 | 0.896 | 0.85 | 10.0468 | Star-Delta | 20.0936 | Identical to P-08, 100% standby.
5 | P-09 | Treated Water Pump | Duty | 12 | 30 | 0.981 | 0.65 | 1.5092 | 1.8111 | 2.2 | 5.5 | 5.5 | 0.896 | 0.85 | 10.0468 | Star-Delta | 20.0936 | Drawing: 10-12 m3/h, 25-30 m. Lifts to elevated tanks at 7.0 m plus DN90 rising main losses.
|  | Total installed motor kW (all pumps) | [9 empty] | 27.5
|  | Total duty motor kW (standby excluded) | [9 empty] | 16.5
|  | Largest single motor (kW) | [9 empty] | 5.5
NOTES
1. Hydraulic power uses the upper end of the flow and head ranges on the drawing, which is conservative.
2. The calculated motor column shows the minimum standard IEC motor that satisfies shaft power x margin. The drawing specifies 5.5 kW for all five pumps.
3. The raw water and treated water pumps calculate to 2.2 kW. 5.5 kW motors give about 2.5x margin; this is acceptable if the vendor pump curve runs out to higher flow, but a 3 kW or 4 kW motor would reduce starting current and cost.
4. The backwash pumps calculate to 5.5 kW at 30 m3/h and 30 m, so the drawing rating is appropriate.
5. Change the 'Electrical design basis' cell on the Inputs sheet to 'Calculated' to re-size all feeders and the incoming supply on the calculated motors.
6. Standby pumps are excluded from maximum demand on the Incoming Supply sheet; they are electrically interlocked with their duty pump.

## Load Schedule
Load Schedule - Motor Control Centre and WTP Control DB
Feeder sizing: FLC -> breaker (next standard size above FLC x factor) -> cable (ampacity after derating >= breaker) -> voltage drop check.
Ckt | Feeder / Load | Load type | Ph | Qty | Unit kW | Connected kW | PF | Eff. | FLC (A) | Running (Y/N) | Diversity | Running input kW | Running kVA | Breaker factor | Breaker calc (A) | Breaker selected (A) | Breaker type | Starter | Cable length (m) | Cable req. (A) | Cable size (mm2) | Cable rating (A) | Volt drop (V) | Volt drop (%) | VD check / Remarks
MCC-1 | Raw Water Pump-1 (Duty) | Motor | 3 | 1 | 5.5 | 5.5 | 0.85 | 0.896 | 10.0468 | Y | 1 | 6.1384 | 7.2216 | 2 | 20.0936 | 25 | MCCB 3P | Star-Delta | 30 | 28.7356 | 2.5 | 30 | 5.4253 | 1.307% | OK - Star-Delta per drawing
MCC-2 | Raw Water Pump-2 (Standby) | Motor | 3 | 1 | 5.5 | 5.5 | 0.85 | 0.896 | 10.0468 | N | 1 | 0 | 0 | 2 | 20.0936 | 25 | MCCB 3P | Star-Delta | 30 | 28.7356 | 2.5 | 30 | 5.4253 | 1.307% | OK - Standby - interlocked with MCC-1
MCC-3 | Backwash Pump (Duty) | Motor | 3 | 1 | 5.5 | 5.5 | 0.85 | 0.896 | 10.0468 | Y | 1 | 6.1384 | 7.2216 | 2 | 20.0936 | 25 | MCCB 3P | Star-Delta | 30 | 28.7356 | 2.5 | 30 | 5.4253 | 1.307% | OK - Counted as running: backwash may overlap with raw water pumping (conservative)
MCC-4 | Backwash Pump (Standby) | Motor | 3 | 1 | 5.5 | 5.5 | 0.85 | 0.896 | 10.0468 | N | 1 | 0 | 0 | 2 | 20.0936 | 25 | MCCB 3P | Star-Delta | 30 | 28.7356 | 2.5 | 30 | 5.4253 | 1.307% | OK - Standby - interlocked with MCC-3
MCC-5 | Treated Water Pump | Motor | 3 | 1 | 5.5 | 5.5 | 0.85 | 0.896 | 10.0468 | Y | 1 | 6.1384 | 7.2216 | 2 | 20.0936 | 25 | MCCB 3P | Star-Delta | 40 | 28.7356 | 2.5 | 30 | 7.2337 | 1.743% | OK - Longest run, to elevated tank side of shelter
DB-1 | Lighting | Lighting | 1 | 1 | 1.5 | 1.5 | 0.9 | 1 | 6.9444 | Y | 0.8 | 1.2 | 1.3333 | 1.25 | 8.6806 | 10 | MCB 1P | - | 25 | 11.4943 | 1.5 | 22 | 5.0347 | 2.098% | OK - Assumed 1.5 kW LED lighting (approx. 11 W/m2 x 132 m2). Drawing: MCB 1P 10A
DB-2 | Socket outlets | Small power | 1 | 1 | 2 | 2 | 0.9 | 1 | 9.2593 | Y | 0.8 | 1.6 | 1.7778 | 1.25 | 11.5741 | 16 | MCB 1P | - | 25 | 18.3908 | 1.5 | 22 | 6.713 | 2.797% | OK - Assumed 2.0 kW allowance. Drawing: MCB 1P 10A
DB-3 | Chemical dosing pumps (PAC, Soda Ash, TCCA, C833/HEDP) | Motor | 1 | 4 | 0.12 | 0.48 | 0.85 | 0.896 | 2.6261 | Y | 1 | 0.53571 | 0.63025 | 2 | 5.2521 | 6 | MCB 1P | DOL | 20 | 6.8966 | 1.5 | 22 | 1.5231 | 0.6346% | OK - Assumed 0.12 kW each diaphragm dosing pump. Drawing: MCB 1P 6A
DB-4 | Agitators (chemical tanks) | Motor | 1 | 4 | 0.37 | 1.48 | 0.85 | 0.896 | 8.097 | Y | 1 | 1.6518 | 1.9433 | 2 | 16.194 | 20 | MCB 1P | DOL | 20 | 22.9885 | 2.5 | 30 | 2.9149 | 1.215% | OK - Assumed 0.37 kW each. Drawing: MCB 1P 6A
DB-5 | Control panel, PLC, level sensors, residual chlorine analyser | Small power | 1 | 1 | 0.5 | 0.5 | 0.9 | 1 | 2.3148 | Y | 1 | 0.5 | 0.55556 | 1.25 | 2.8935 | 6 | MCB 1P | - | 10 | 6.8966 | 1.5 | 22 | 0.6713 | 0.2797% | OK - Not shown on drawing - added as assumed load for auto operation
DB-6 | Spare | Small power | 1 | 1 | 0.5 | 0.5 | 0.9 | 1 | 2.3148 | N | 1 | 0 | 0 | 1.25 | 2.8935 | 6 | MCB 1P | - | 20 | 6.8966 | 1.5 | 22 | 1.3426 | 0.5594% | OK - Spare way. Drawing: MCB 1P 6A
| TOTAL |  |  |  |  | 33.96 |  |  | 38.8217 |  |  | 23.9027 | 27.9051
LEGEND
Blue = input. Green = linked from another sheet. Black = formula. Yellow fill = assumed load value not given on the drawing - confirm with vendor.
FLC (A): 3-phase = kW x 1000 / (sqrt3 x V x PF x eff); 1-phase = kW x 1000 / (V_LN x PF x eff).
Breaker: next standard rating above FLC x factor (2.0 for motors with starter overload relay, 1.25 otherwise).
Cable: smallest size whose ampacity x derating factor is at least the breaker rating, so the breaker protects the cable.
Voltage drop = mV/A/m x FLC x length / 1000, checked against the limit on the Inputs sheet. Single-phase circuits use the 4-core table values, which is conservative.
Single-phase DB loads are to be distributed across R, Y, B phases as evenly as possible; the DB is a 3-phase board fed from the MCC.
Note on J16: Maximum demand current, 3-phase equivalent, assuming single-phase loads are balanced across phases.

## Incoming Supply
Incoming Power Supply Sizing - Main MCCB, Incoming Cable, TNB Supply and Standby Generator
All values derive from the Load Schedule and Inputs sheets.
Item | Value | Unit | Formula / Basis
A. CONNECTED AND RUNNING LOAD
Total connected load (all feeders incl. standby) | 33.96 | kW | Sum of connected kW on Load Schedule
Maximum demand - running input power | 23.9027 | kW | Running loads only, standby pumps excluded, diversity applied to lighting and small power, motor efficiency included
Maximum demand - apparent power | 27.9051 | kVA | Sum of running kVA
Overall power factor at maximum demand | 0.85657 | - | kW / kVA
Maximum demand current | 38.8217 | A | kVA x 1000 / (sqrt3 x 415)
B. INCOMING SUPPLY DESIGN CURRENT
Spare capacity allowance | 0.25 | - | From Inputs
Design current including spare capacity | 48.5272 | A | Max demand current x (1 + spare)
Largest motor FLC | 10.0468 | A | Largest of the MCC motor feeders
Largest motor starting current (Star-Delta) | 20.0936 | A | FLC x Star-Delta starting multiple
Peak current during start of largest motor | 48.8685 | A | Max demand current with the largest motor replaced by its starting current (other loads running). Main MCCB must not trip at this value.
C. MAIN INCOMING MCCB
Main MCCB required rating (next standard size) | 50 | A | Next standard rating above design current
Main MCCB shown on drawing | 225 | A | Drawing: Main MCCB 4P 225A
Drawing MCCB utilisation at maximum demand | 17.25% | % | Max demand current / drawing MCCB rating
Recommended main MCCB | 63 | A | Calculated rating, but not less than 63 A (4-pole, with adjustable thermal setting, SPD Type 2 downstream, earth bar). Set thermal trip to design current.
Assessment of drawing 225 A MCCB | Adequate - oversized by 4.5x; acceptable if TNB connected load and metering CT are matched, otherwise reduce to recommended rating | - | Comparison
D. INCOMING CABLE (TNB meter board to MCC)
Incoming cable length | 25 | m | ASSUMED distance from TNB metering/main switch to MCC room. Edit.
Required cable ampacity (recommended MCCB / derating) | 72.4138 | A | Cable must be protected by the main MCCB
Incoming cable size - Cu XLPE/SWA/PVC 4-core | 16 | mm2 | Smallest standard size meeting required ampacity
Incoming cable rating | 94 | A
Voltage drop at design current | 3.3969 | V | mV/A/m x design current x length
Voltage drop | 0.8185% | % | Limit for sub-main: see Inputs. Total from origin to motor terminals should stay within 5%.
Voltage drop check | OK | -
E. TNB SUPPLY APPLICATION
Supply type | 415 V, 3-phase, 4-wire, 50 Hz LV supply | - | Per drawing
Declared maximum demand for TNB application | 35 | kVA | Max demand kVA x (1 + spare), rounded up
Connected load declared | 34 | kW
Indicative tariff category | LV Commercial / Industrial (below 100 kVA class) | - | Indicative only - confirm with TNB regional office; actual tariff code depends on premises classification
Energy consumption estimate | 4302.4821 | kWh/month | Max demand kW x running hours/day x days/month (upper bound; backwash does not run all day)
Energy cost estimate | 2189.9634 | RM/month | kWh x assumed tariff (Inputs)
F. STANDBY GENERATOR (optional, if required by client)
Running load | 27.9051 | kVA | Max demand kVA
Starting kVA of largest motor (Star-Delta) | 14.4433 | kVA | sqrt3 x V x starting current / 1000
Transient demand (running load minus largest motor plus its starting kVA) | 35.1268 | kVA | Worst case: largest motor starts with everything else running
Generator sizing basis | 35.1268 | kVA | Greater of running load x 1.25 and transient demand
Recommended generator (next standard size) | 40 | kVA | Standard prime-rated set sizes; 415 V, 3-phase, with ATS at main incoming
NOTES
1. Maximum demand counts the raw water duty pump, backwash duty pump, treated water pump, lighting, sockets, dosing pumps, agitators and controls as running together. Standby pumps are interlocked and excluded.
2. The 225 A main MCCB on the drawing is far above the calculated demand. It is harmless electrically, but TNB applications are assessed on declared maximum demand, and a 225 A frame implies ~160 kVA which may push the installation into CT metering and a higher connection charge. Confirm the intended future expansion before keeping 225 A.
3. All motor feeders use Star-Delta starters per the drawing; with calculated 2.2 kW motors for the raw and treated water pumps, DOL starting would be acceptable and simpler.
4. Earthing: single earth bar in MCC, all equipment and DBs bonded. SPD Type 2 at main incoming per drawing. Earth electrode resistance target 1 ohm or less; TT or TN-C-S per TNB supply arrangement.
5. All assumed values are highlighted yellow on the Inputs and Load Schedule sheets. Replace them with vendor data and the workbook recalculates.